## Slide 1: Benchmark process
January 21, 2022

## Slide 2
S4 – Grit/screenings to landfill
S19 – Biosolids
Pumping station
Preliminary treatment
(Grit)
Secondary
treatment
(Activated sludge
and clarifier)
Disinfection
(Chlorination)
Primary treatment
(Clarifier)
S12 – Treated water
Gravity thickening
Anaerobic digestion
Other buildings
(Control, laboratory, etc.)
S1 –
Waste
water
S2
S3
S5
S17
S13
S20
S7
S10
S9
S14
S16
S21
Dewatering
(Filter press)
S8 – Air
Benchmark – Introduction
S6
  Conventional wastewater treatment plant with activated sludge process
S11 –
Chlorine
S18 –
Lime and polymer
Reference
1) Qasim, Syed R. “Wastewater treatment plants: planning, design, and operation”. (1985).
Boiler
S15 – Biogas#
BOD5: Biochemical oxygen demand
TSS: Total suspended solids

## Slide 3
S4 – Grit/screenings to landfill
S19 – Biosolids
Pumping station
Preliminary treatment
(Grit)
Disinfection
(Chlorination)
Primary treatment
(Clarifier)
S12 – Treated water
Gravity thickening
Anaerobic digestion
Other buildings
(Control, laboratory, etc.)
S1 –
Waste
water
S2
S3
S5
S17
S13
S20
S7
S10
S9
S14
S16
S21
Dewatering
(Filter press)
S8 – Air
Benchmark – Design and performance
S6
BOD5 removal: 34%
TSS removal: 63%
BOD5 removal: 89%
TSS removal: 85%
Secondary
treatment
(Activated sludge
and clarifier)
  Plant Capacity: 38016 m3/d
  Removal efficiency
    BOD5: 92.0%; TSS: 92.3%
0.25
0.26
0.2
0.2
Units
BOD5 [kg/m3]
TSS [kg/m3]
S11 –
Chlorine
S18 –
Lime and polymer
Reference
1) Qasim, Syed R. “Wastewater treatment plants: planning, design, and operation”. (1985).
Boiler
S15 – Biogas#
Biogas production
: 0.37 m3/kg TSS
  Biogas production
    Digestion period: 15 d
    Potential biogas production
    : 0.37 m3/kg TSS
    # 84% of produced biogas is used to supply
    heating energy for anaerobic digestion.
BOD5: Biochemical oxygen demand
TSS: Total suspended solids

## Slide 4
S4 – Grit/screenings to landfill
0.7
S19 – Biosolids
Pumping station
Preliminary treatment
(Grit)
Disinfection
(Chlorination)
Primary treatment
(Clarifier)
S12 – Treated water
Gravity thickening
Anaerobic digestion
Other buildings
(Control, laboratory, etc.)
419
S1 –
Waste
water
S2
S3
S5
S6
S17
S13
S20
S7
S10
S9
S14
S16
S21
38016
38016
38016
37882
38511
38000
510
629
134
112
S15 – Biogas#
532
31
66
Dewatering
(Filter press)
15
81
S8 – Air
853125
S18 –
Lime and polymer
38000
S11 –
Chlorine
Benchmark – Pollutant concentrations
Secondary
treatment
(Activated sludge
and clarifier)
190
Units
Volume flow [m3/d]
286
BOD5 removal: 34%
TSS removal: 63%
BOD5 removal: 89%
TSS removal: 85%
Reference
1) Qasim, Syed R. “Wastewater treatment plants: planning, design, and operation”. (1985).
Biogas production
: 0.37 m3/kg TSS
Boiler
2141
BOD5: Biochemical oxygen demand
TSS: Total suspended solids
0.250
0.250
0.250
0.166
0.185
0.020
2.359
1.362
24.112
67.125
1.250
3.000
1.500
75.867
15.272
0.020
BOD5 [kg/m3]
0.260
0.260
0.260
0.097
0.137
0.020
3.747
2.579
46.470
61.759
2.295
4.032
4.182
272.667
50.370
0.020
TSS [kg/m3]

## Slide 5
S4 – Grit/screenings to landfill
0.7
S19 – Biosolids
Pumping station
Preliminary treatment
(Grit)
Disinfection
(Chlorination)
Primary treatment
(Clarifier)
S12 – Treated water
Gravity thickening
Anaerobic digestion
Other buildings
(Control, laboratory, etc.)
419
S1 –
Waste
water
S2
S3
S5
S6
S17
S13
S20
S7
S10
S9
S14
S21
38016
38016
38016
37882
38511
38000
510
629
134
112
S15 – Biogas#
532
31
66
Dewatering
(Filter press)
15
81
S8 – Air
853125
S18 –
Lime and polymer
38000
S11 –
Chlorine
Benchmark – Mass balance
Secondary
treatment
(Activated sludge
and clarifier)
190
Units
Volume flow [m3/d]
Chemical mass flow [kg/d]
286
  Water recovery: >99%
  Biogas production#: 419 m3/d
    Initial production: 2560 m3/d
    Combustion for heat supply: 2141 m3/d
BOD5 removal: 34%
TSS removal: 63%
BOD5 removal: 89%
TSS removal: 85%
Reference
1) Qasim, Syed R. “Wastewater treatment plants: planning, design, and operation”. (1985).
Biogas production
: 0.37 m3/kg TSS
Boiler
2141
9504
9504
9504
6273
7130
760
1203
857
3231
7518
665
93
99
1138
1237
760
BOD5 mass flow [kg/d]
9884
9884
9884
3657
5279
760
1911
1622
6227
6917
1221
125
276
4090
4080
760
TSS mass flow [kg/d]
BOD5: Biochemical oxygen demand
TSS: Total suspended solids
S16

## Slide 6
S4 – Grit/screenings to landfill
0.7
S19 – Biosolids
Pumping station
Preliminary treatment
(Grit)
Disinfection
(Chlorination)
Primary treatment
(Clarifier)
S12 – Treated water
Gravity thickening
Anaerobic digestion
Other buildings
(Control, laboratory, etc.)
S1 –
Waste
water
S2
S3
S5
S6
S17
S13
S20
S7
S10
S9
S14
S21
38016
9504
9884
38016
9504
9884
38016
9504
9884
37882
6273
3657
38511
7130
5279
38000
760
760
510
1203
1911
629
857
1622
134
3231
6227
112
7518
6917
532
665
1221
66
99
276
Dewatering
(Filter press)
15
1138
4090
81
1237
4080
S8 – Air
853125
38000
760
760
S11 –
Chlorine
Benchmark – Energy requirements
2200
280
300
7900
46
460
2520
14
Secondary
treatment
(Activated sludge
and clarifier)
Units
Volume flow [m3/d]
Chemical mass flow [kg/d]
BOD5 mass flow [kg/d]
TSS mass flow [kg/d]
Electricity [kWh/d]
Heat [kWh/d]
190
S18 –
Lime and polymer
286
Wastewater
treatment
1.00
Wastewater
1.00
Treated
water
0.390
Boiler
Water
[m3/d]
Biogas
[m3/d]
0.056
0.285
Electricity [kWh/(m3/d)]
Heat [kWh/(m3/d)]
10840
Reference
2) Pabi, S., et al. "Electricity use and management in the municipal water supply and wastewater industries." (2013).
0.011
Biogas
419
S15 – Biogas#
Boiler
2141
1100
BOD5: Biochemical oxygen demand
TSS: Total suspended solids
S16
93
31
125

## Slide 7
S4 – Grit/screenings to landfill
0.7
S19 – Biosolids
Pumping station
0.048
(0.037/0.011)
Preliminary treatment
0.028
(0.025/0.004)
Disinfection
0.023
(0.019/0.004)
Primary treatment
0.046
(0.040/0.006)
S12 – Treated water
Gravity thickening
0.026
(0.023/0.003)
Anaerobic digestion
0.170
(0.148/0.022)
Other buildings
0.065
(0.052/0.013)
S1 –
Waste
water
S2
S3
S5
S6
S17
S13
S20
S7
S10
S9
S14
S16
S21
38016
9504
9884
38016
9504
9884
38016
9504
9884
37882
6273
3657
38511
7130
5279
38000
760
760
510
1203
1911
629
857
1622
134
3231
6227
112
7518
6917
532
665
1221
31
93
125
66
99
276
Dewatering
0.081
(0.052/0.029)
15
1138
4090
81
1237
4080
S8 – Air
853125
38000
760
760
S11 –
Chlorine
Benchmark – Treatment costs
2200
280
300
7900
46
460
2520
14
Secondary
Treatment
0.233
(0.193/0.040)
BOD5: Biochemical oxygen demand
TSS: Total suspended solids
Units
Volume flow [m3/d]
Chemical mass flow [kg/d]
BOD5 mass flow [kg/d]
TSS mass flow [kg/d]
Electricity [kWh/d]
Heat [kWh/d]
190
S18 –
Lime and polymer
286
10840
Reference
3) EPA. “Construction Costs for Municipal Wastewater Treatment Plants: 1973-1978 ." (1980).
4) EPA, “Costs and Manpower for Municipal Wastewater Treatment Plant Operation and Maintenance, 1965-1968” (1978)
419
S15 – Biogas#
Boiler
2141
1100
Unit process
Total cost [$/m3]
(capital/operating)
Wastewater
Treatment
0.913
(0.760/0.153)
1.00
Wastewater
1.00
Treated
water
Water
[m3/d]
Biogas
[$/(m3/d)]
0.001
Biogas
0.198
(0.175/0.023)